DEF: Wafer butterfly valve, tightly-closing, nominal pressure 16 bar

For continuous control of water, air and low-pressure steam flow up to 110 °C.

Butterfly body made of cast iron (GG25) to fit flanges PN 6, PN 10 and PN 16; blue hammer- enamel finish. Drive flange acc. to EN ISO 5211. Butterfly disc made of stainless steel. Ethylene-propylene rubber collar. Stainless-steel spindle sealed with 2 O-ring packings.

| Type | Nominal width DN | kVS value m3/h | Weight kg |  |
| --- | --- | --- | --- | --- |
| DEF 025 F200 | 25 | 36 | 1 |  |
| DEF 032 F200 | 32 | 40 | 1.15 |  |
| DEF 040 F200 | 40 | 50 | 2.75 |  |
| DEF 050 F200 | 50 | 85 | 3.05 |  |
| DEF 065 F200 | 65 | 215 | 4.05 |  |
| DEF 080 F200 | 80 | 420 | 4.30 |  |
| DEF 100 F200 | 100 | 800 | 4.85 |  |
| DEF 125 F200 | 125 | 1010 | 7.20 |  |
| DEF 150 F200 | 150 | 2100 | 9.50 |  |
| DEF 200 F200 | 200 | 4000 | 12 |  |
| Nominal pressure | PN 16 | Dimension drawings | 5M109 |
| Max. perm. operating pressure | 16 bar |  |  |
| Control characteristic | linear | Fitting instructions | MV 505826 |
| Angle of butterfly rotation | 90° | Assembly ASF | MV 505833 |
| Leakage rate | < 0,0001 % of kvs | Assembly AR30 | MV 505831 |
| Permissible operating temperature | –10...130 °C | Assembly A44 | MV 505832 |
| Accessories |  |
| 361632 . . . | 2 counter flanges compl. PN 6 acc. to VSM 18716 (DIN 2631) |  |
|  | DN | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 125 | 150 | 200 |  |
| 361633 . . . | 2 counter flanges compl. PN 10 (DN 25...150) acc. to |  |
|  | VSM 18717 (DIN 2632) and PN 16 (DN 25...200) acc. to VSM 18718 (DIN 2633) |  |
|  | DN | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 125 | 150 | 200 |  |
|  | Specify when ordering: DN 25 = /025, DN 100 = /100 |  |
| 361634 200 | 2 counter flanges compl. PN 10 (DN 200) acc. to VSM 18717 (DIN 2632) |  |
| 361734 001 | Butterfly body outside surfaces, cold galvanized DN 25...125 |  |
| 361734 002 | Butterfly body outside surfaces, cold galvanized DN 150, 200 |  |
| 378108 001 | Assembly kit; DEF DN 25-65 für AR 30 |  |
| 378109 001 | Assembly kit; DEF DN 80-100 für AR 30 |  |
| 378110 001 | Assembly kit; DEF DN 25-65 für A44 |  |
| 378111 001 | Assembly kit; DEF DN 80-125 für A 44 |  |
| 378112 001 | Assembly kit; DEF DN 150-200 für A44 |  |
| 378113 001 | Assembly kit; DEF DN 25-100 für ASF 122/123 |  |

7 154008 003  Q2

| Combination with actuator with return spring: |
| --- |
| Drive 1) | Input Running time Safety function | ASF 122 F120 2-point 90 s 15 s | ASF 123 F122 3-point 90 s 15 s | ASF 123S F122 0...10 V 90 s 15 s |  |
| Butterfly valve: | p 2) | p 3) |  |  |  |  |
| DEF 025 F200 | 10 | 10 |  |  |  |  |
| DEF 032 F200 | 10 | 10 |  |  |  |  |
| DEF 040 F200 | 10 | 10 |  |  |  |  |
| DEF 050 F200 | 10 | 10 |  |  |  |  |
| DEF 065 F200 | 7 | 7 |  |  |  |  |
| DEF 080 F200 | 4 | 4 |  |  |  |  |
| DEF 100 F200 | 2 | 2 |  |  |  |  |
| 1) | Assembly kit 378113 001 required (weight 0.5 kg) |  |
| 2) | Max. permissible pressure difference in bar |  |
| 3) | Max. differential pressure at the butterfly valve in bar (in the event of malfunction) at which the drive can still close the butterfly. |  |

Combination with electric motor drive AR30 W2.

| Drive 1) | Input Running time | AR30 W23 3-point 120 s | AR30 W23S 0...10 V 120 s |  |  |
| --- | --- | --- | --- | --- | --- |
| Butterfly valve | p 2) |  |  |  |  |
| DEF 025 F200 | 10 |  |  |  |  |
| DEF 032 F200 | 10 |  |  |  |  |
| DEF 040 F200 | 10 |  |  |  |  |
| DEF 050 F200 | 10 |  |  |  |  |
| DEF 065 F200 | 7 |  |  |  |  |
| DEF 080 F200 | 4 |  |  |  |  |
| DEF 100 F200 | 2 |  |  |  |  |
| 1) | For DN 25...65: Assembly kit 378108 001 required (weight 0.4 kg) For DN 80 and 100: Assembly kit 378109 001 required (weight 0.4 kg) |
| 2) | Permissible pressure difference in bar |

Combination with electric motor drive A44

| Drive 1) | Input Running time | A44 W2 3-point 120 s | A44 W2S 0...10 V 120 s |  |
| --- | --- | --- | --- | --- |
| Butterfly valve | p 2) |  |  |  |
| DEF 025 F200 | 10 |  |  |  |
| DEF 032 F200 | 10 |  |  |  |
| DEF 040 F200 | 16 |  |  |  |
| DEF 050 F200 | 16 |  |  |  |
| DEF 065 F200 | 16 |  |  |  |
| DEF 080 F200 | 10 |  |  |  |
| DEF 100 F200 | 10 |  |  |  |
| DEF 125 F200 | 6 |  |  |  |
| DEF 150 F200 | 5 |  |  |  |
| DEF 200 F200 | 3 |  |  |  |
| 1) | For DN 25...65: Assembly kit 378110 001 required (weight 0.2 kg) For DN 80...125: Assembly kit 378111 001 required (weight 0.2 kg) For DN 150 and 200: Assembly kit 378112 001 required (weight 0.2 kg) |
| 2) | Permissible pressure difference in bar |
| Complete type designation: | Butterfly valve and drive with corresponding F-version |
| Butterfly valve: | F-version, technical data and accessories: see table of types on page 1 |
| Drive: | F-version, technical data and accessories: see section 51 |
| Example: | DEF 65 F200/ASF 123S F122 |

7 154008 003  Q2

Operation

Can be actuated by means of motor drive or actuator with spring-return action to attain any intermediate position. Can be used as a safety device in conjunction with actuator ASF 12. In this case, the butterfly is actuated such that it will move either to its closed or open position in the event of a power failure or whenever a limiter comes into operation.

Manual butterfly adjustment:

- AR30	by means of a hand crank (mounted in the adapter plate)

- A44 W	by means of a hand crank (mounted under the hood)

- ASF 12	manually after the coupling has been released

Information for engineering and installation

The butterfly valve is installed by clamping and then screw-mounting the unit between two flanges. The butterfly must be opened to at least 10 % during installation. A special lining of the housing eliminates the need for flange gaskets.

Flow admission is possible from either side.

Additional design information

Design length of the butterfly valve acc. to EN 558 series 20 from nominal diameter 40. Collar is lined such that no contact between cast iron medium is possible.

Drive flange acc. to EN ISO 5211 NFE 29-402

Flange accommodation acc. to DIN 2501

7 154008 003  Q2

| DN | Directive on pressure equipment | CE |
| --- | --- | --- |
| 25 | 93 / 23 / EG | Art. 33 | – |
| 32 | 93 / 23 / EG | Art. 33 | – |
| 40 | 93 / 23 / EG | Art. 33 | – |
| 50 | 93 / 23 / EG | Art. 33 | – |
| 65 | 93 / 23 / EG | Cat. I | CE |
| 80 | 93 / 23 / EG | Cat. I | CE |
| 100 | 93 / 23 / EG | Cat. I | CE |
| 125 | 93 / 23 / EG | Cat. I | CE |
| 150 | 93 / 23 / EG | Cat. I | CE |
| 200 | 93 / 23 / EG | Cat. I | CE |

Dimension drawings 5M109

DEF 25...65

DEF 80...200

Printed in Switzerland
Right of amendment reserved
N.B.: A comma between cardinal
numbers denotes a decimal point
© Fr. Sauter AG, CH-4016 Basle
7 154008 003  Q2

with drive A44

with drive AR30

DN 25...100 with drive ASF 122, ASF 123